## Intro
This spreadsheet describes resources relevant to the 2024 DLC RFP fNLC-HVAC Toolkit.
The "General" worksheet has 3 guidelines for NLC-HVAC integration, plus other resources
The "Case study summary" worksheet includes the US and Canada.
The "Case study details" work in progress worksheet has details from some case studies, including some international that are not in the summary worksheet
The "Lessons Learned" worksheet is excerpted from some of the case studies

## General
Document type | Pages | Description | URL
DLC NLC QPL spreadsheet of product data | 1 | The DLC Networked Lighting Control Qualified Products List (DLC QPL) has data about many capabilities of over 60 NLC systems. To see all of the available data fields, download the spreadsheet. After logging into designlights.org with a free acount, at the URL choose "Add All Results to My List" then "DOWNLOAD MY LIST" | https://qpl.designlights.org/qpl/networked-lighting-controls
Integration Guidelines | 16 | "Hot Mess or Cool Tech? Secrets to Success for Advanced Buil;ding Controls Integration", N.Hinkle, R. Mead, B. Kirlin. Cadmus. ACEEE 2022 Summer Study. HVAC and Lighting controls integration is challenging. Is it worthwhile? Lessons learned from pilot of 5 case studies in Minnesota with PNNL and Xcel Energy. | https://aceee2022.conferencespot.org/event-data/pdf/catalyst_activity_32392/catalyst_activity_paper_20220810190501262_6e1bd41a_890c_4fc8_87ab_e353845d0cba
Integration Guidelines | 39 | A guide for successful integration of NLC, HVAC and plug load controls | https://slipstreaminc.org/publications/integrated-controls-implementation-guide
Integration Guidelines | 30 | Opportunities to integrate lighting with other systems in your building. PNNL-SA-172234 | https://www.utilityforum.org/Data/Sites/7/media/presentations/myer-lighting-integration.pdf
presentation | 31 | "Facilitating the Operation of Smart Buildings through Instrumentation, Monitoring and Data", Scott Hackel, Sliptream, ASHRAE 2020 Virtual Conference, Seminar 63. Lessons learned from pilot of 5 case studies in Minnesota with PNNL and Xcel Energy. | https://store.accuristech.com/3a/standards/seminar-63-facilitating-the-operation-of-smart-buildings-through-instrumentation-monitoring-and-data?product_id=2188928
Title 24 case report | 402 | "2022 Title 24, Part 6 Final CASE Report Addendum – 2022-NR-LIGHT2-F" California Title 24 CASE Report on Occupied Standby Mode, pp16-33 | https://title24stakeholders.com/2022-cycle-case-reports/
Title 24 code | 2 | Excerpt from California Title 24 2022 Multifamily and Nonresidential Compliance Manual, section 4.4.11 Occupant Sensor Ventilation Control Devices | https://www.energy.ca.gov/filebrowser/download/5107
whitepaper | 43 | NLC systems capable of communicating with other building systems maximize energy efficiency and savings | https://www.designlights.org/news-events/news/new-dlc-report-webinar-interoperability-for-networked-lighting-controls/

## Case study summary
State/ Prov. | Case Study Site | Type & Number of Buildings | Internet URL
MN | Hennepin County | Clinic & Fitness | https://integratedlightingcampaign.energy.gov/sites/default/files/2023-07/EED_2406_FLYER_Hennepin-FieldVal_FINAL2.pdf
CA | Cal State Dominguez Hills | College | https://newbuildings.org/wp-content/uploads/2021/05/Retrofit-Tech-Case-Study_CSU_FINALv5.pdf
CA | Cal State Long Beach | College, 110 | https://www.enlightedinc.com/wp-content/uploads/2023/02/Enlighted_Case-Study_CSU-Long-Beach_r4.pdf
CA | UC Davis | College, 4 | https://www.energy.ca.gov/sites/default/files/2023-06/CEC-500-2023-039.pdf
MN | University of MN | College | https://integratedlightingcampaign.energy.gov/sites/default/files/2023-07/EED_1581_FLYER_UM-FieldVal_FINAL2.pdf
MN | CentraCare Becker | Healthcare | https://integratedlightingcampaign.energy.gov/sites/default/files/2023-07/EED_2282_FLYER_CentraCare-FieldVal_FINAL2.pdf
CA | Kaiser San Diego | Healthcare, 10 | https://www.willdan.com/casestudies/Kaiser-Permanente-HVAC-Case-Study.pdf
TX | Sinclair Hotel | Hotel | https://www.mncee.org/sites/default/files/report-files/EE0008191_PoE_Case_Study_SinclairHotel.pdf
WA | Enatai Elementary | K-12 | https://atspnw.com/projects/integrated-lighting-hvac/
WA DC | KIPP DC | K-12, 20 | https://www.nexuslabs.online/content/case-study-kipp-dc-schools-wants-autonomy-deploys-idl-supervisory-control-fdd-and-cmms
ON | Cisco Toronto | Office | https://www.panduit.com/content/dam/panduit/en/solutions/solution-pdf/NI-ENT-CiscoCaseStudy_CPCS64.pdf
MN | City of St Paul | Office | https://integratedlightingcampaign.energy.gov/sites/default/files/2023-07/EED_2407_FLYER_StPaul-FieldVal_FINAL2.pdf
CO | Denver Water Admin | Office | https://betterbuildingssolutioncenter.energy.gov/sites/default/files/attachments/ILC-Case%20Study-DenverWater.pdf
NY | Empire State Building | Office | https://www.lutron.com/CaseStudyLibrary/ESB_English.pdf
CA | Intuit San Diego | Office | https://www.ibismsi.com/occupancy-enabled-hvac-optimization-case-study/
NY | Penn 1 Plaza | Office | https://www.cisco.com/c/en/us/solutions/collateral/enterprise-networks/dna-spaces/cisco-penn1-case-study.pdf
WA DC | Theodore Roosevelt Federal Building | Office | https://betterbuildingssolutioncenter.energy.gov/sites/default/files/attachments/ILC-Case%20Study-OPM.pdf
CA | Menlo Business Park | Office & Lab | https://www.enlightedinc.com/wp-content/uploads/2022/09/Enlighted_Casestudy_Menlo-Rev01.pdf
OK | Tinker AFB | Open ofc. & Indus. | https://integratedlightingcampaign.energy.gov/sites/default/files/2021-02/EED_1063_BROCH_ESTCPbrand.pdf
MN | MN DOT Cedar Ave, Better Buildings | Open office | https://betterbuildingssolutioncenter.energy.gov/sites/default/files/attachments/ILC_Case_Studies_MnDOT.pdf
MN | MN DOT Cedar Ave, Slipstream | Open office | https://slipstreaminc.org/publications/case-study-state-minnesota-department-transportation
NC | Crate & Barrel Durham | Retail | https://www.shareddocs.com/hvac/docs/1001/Public/09/CASESTUDY63.pdf
- | ECOMT | Retail, 3400 | https://www.intesis.com/docs/librariesprovider11/case-studies/ecomt_success-story_2020.pdf
- | ATT | Various, 240 | https://www.enlightedinc.com/wp-content/uploads/2022/09/Enlighted_Casestudy_ATT_p1r2.pdf
MN | Cadmus | Various, 5 | https://aceee2022.conferencespot.org/event-data/pdf/catalyst_activity_32392/catalyst_activity_paper_20220810190501262_6e1bd41a_890c_4fc8_87ab_e353845d0cba

## Case study details
Organization | Efficiency Program | NLC brand | Real or Model? | Reference | Internet URL | Country | State | Site | Building Type | Year Pub. | Project sq ft | Hours of Use | HVAC zone size | Type of HVAC | Energy saved | Pay back yr | Details about Payback | Notes
PNNL | - |  | Model | PNNL-22072 Case 2 | https://www.pnnl.gov/main/publications/external/technical_reports/PNNL-22072.pdf?bcsi_scan_C429A8BD0F8CBB7E=0&bcsi_scan_filename=PNNL-22072.pdf |  | all | All US climate zones | Office | 2013 | Large |  | 2,200 to 27,000 | VAV terminal box airflow set to 0 when unoccupied | 6% of bldg |  |  | Savings is average national in large office buildings
PNNL | - |  | Model | PNNL-22072 Case 3 | https://www.pnnl.gov/main/publications/external/technical_reports/PNNL-22072.pdf?bcsi_scan_C429A8BD0F8CBB7E=0&bcsi_scan_filename=PNNL-22072.pdf |  | all | All US climate zones | Office | 2013 | Large |  | 2,200 to 27,000 | VAV terminal box airflow reduced proportionally when occupant count is lower than max. | 18% of bldg |  |  | Savings is average national in large office buildings
PNNL, Slipstream | Xcel | Cree | Real |  | https://betterbuildingssolutioncenter.energy.gov/sites/default/files/attachments/ILC_Case_Studies_MnDOT.pdf | United States | MN | DoT truck facility | open office? |  | 11300 | 24/7 | 11300 | VAV 10 zones with hot water reheat coils and fan speed control regulators | 14 kWh/sf | 3.7 |  | -Annual energy saved with retrofitted luminaires: 19,036 kWh -Total controlled outlets: 13 -Annual plug load energy saved in controlled outlets: 774 kWh -Plug load material cost: $1,654 -Plug load labor cost: $556
PNNL, Slipstream | Xcel | Cree | Real |  | https://integratedlightingcampaign.energy.gov/sites/default/files/2023-07/EED_2282_FLYER_CentraCare-FieldVal_FINAL2.pdf | United States | MN | CentraCare | clinic | 2021 | 12400 | 45 h/wk | 12400 | VAV air handling unit Most are hot water reheat boxes | 1.65kWh/sf | 32.7 | HVAC payback not listed, lighting payback used instead | 57% lighting potential savings 46% potential plug load savings
PNNL, Slipstream | Xcel | Cree | Real |  | https://integratedlightingcampaign.energy.gov/sites/default/files/2023-07/EED_2407_FLYER_StPaul-FieldVal_FINAL2.pdf | United States | MN | City of St Paul | office | 2021 | 13100 | 45 h/wk | 13100 | Two dual duct multi zone constant air volume AHU | 1.7kWh/sf | 44.7 | HVAC payback not listed, total project payback used instead | 63% potential lighting savings 56% potential plug load savings
PNNL, Slipstream | Xcel | Cree | Real |  | https://integratedlightingcampaign.energy.gov/sites/default/files/2023-07/EED_2406_FLYER_Hennepin-FieldVal_FINAL2.pdf | United States | MN | Hennepin fit / clinic | healthcare | 2021 | 7300 |  | 7300 | VAV air handling unit Most are hot water reheat boxes | 1.5kWh/sf | 6.6 | Hvac payback listed | 63% potential lighting savings 56% potential plug load savings
PNNL, Slipstream | Xcel | Cree | Real |  | https://integratedlightingcampaign.energy.gov/sites/default/files/2023-07/EED_1581_FLYER_UM-FieldVal_FINAL2.pdf | United States | MN | Univ MN | school | 2022 | 25000 | 75+ h/wk | 25000 | ` | .88 kWh | 3.2 | Hvac payback listed | 57% potential lighting savings 32% potential plug load savings 36% potential HVAC savings
PNNL | DOD | Enlighted | Real | PNNL-SA-158737 | https://integratedlightingcampaign.energy.gov/sites/default/files/2021-02/EED_1063_BROCH_ESTCPbrand.pdf | United States | OK | Tinker AFB | open office | 2021 | 5000 |  |  |  | 12% of mech | 7.3 | whole project, ofc + indus | energy saved is ambiguous. Probably % of mechanical, although text top of p.4 says "building energy savings of 26%"
PNNL | DOD | Enlighted | Real | PNNL-SA-158737 | https://integratedlightingcampaign.energy.gov/sites/default/files/2021-02/EED_1063_BROCH_ESTCPbrand.pdf | United States | OK | Tinker AFB | industrial | 2021 | 21000 |  |  |  | 30% of mech | 7.3 | whole project, ofc + indus
IBIS |  |  | Real |  | https://www.ibismsi.com/occupancy-enabled-hvac-optimization-case-study/ |  | ? |  | hybrid office | 2022 |  |  |  |  | 15% of bldg 30% of HVAC | 2 to 3 | Connect existing NLC & HVAC
IBIS |  |  | Real |  | https://www.ibismsi.com/occupancy-enabled-hvac-optimization-case-study/ | United States | CA | Intuit campus, San Diego | [6 empty] | 20%+ of bldg | 2.5 |  | Savings from HVAC-occ plus continuous commissioning
NBI | EPIC | Enlighted | Real |  | https://newbuildings.org/wp-content/uploads/2021/05/Retrofit-Tech-Case-Study_CSU_FINALv5.pdf | United States | CA | California State University Dominguez Hills | school | 2017 |  |  |  | VAV | 29% savings from HVAC |  |  | 26% overall site savings from lighting and HVAC retrofit
|  | Lutron | Real |  | https://www.lutron.com/CaseStudyLibrary/ESB_English.pdf | United States | NY | Empire State Building | Office | 2012 | [5 empty] | 2.7 | Overall Project Payback
DOE ILC |  |  | Real |  | https://betterbuildingssolutioncenter.energy.gov/sites/default/files/attachments/ILC-Case%20Study-DenverWater.pdf | United States | CO | Denver Water Admin Buidling | Office | 2019 | [7 empty] | Covid delays resulted in savings results not yet being available Estimated annual energy savings of 25000
DOE ILC |  | Lutron | Real |  | https://betterbuildingssolutioncenter.energy.gov/sites/default/files/attachments/ILC-Case%20Study-OPM.pdf | United States | DC | Theodore Roosevelt Federal Building | Office |  | 50000 |  |  |  | 965,979 kWh saved |  |  | Phase 3 of the project is ongoing Above $100,000 saved annually after phase 2
Willdan |  |  | Real |  | https://www.willdan.com/casestudies/Kaiser-Permanente-HVAC-Case-Study.pdf | United States | CA |  | healthcare | [5 empty] | 8,897,991 kwh | 1.8 |  | This is a multi facility project $1,177,300 Utility
|  |  | Real |  | chrome-extension://efaidnbmnnnibpcajpcglclefindmkaj/https://www.shareddocs.com/hvac/docs/1001/Public/09/CASESTUDY63.pdf | United States | NC | Crate & Barrel Durham, NC | Retail | 2010 | 25000 | [6 empty] | The control system in place at the Durham store, in combination with a lighting re-design, has reduced usage from Crate&Barrel’s previous average of 12 W/ft2 to 6W/ ft2 while maintaining the company’s preferred levels of comfort and product display. The store has also returned a 70 percent reduction in HVAC costs over earlier stores.
|  |  | Real |  | https://atspnw.com/projects/integrated-lighting-hvac/ | United States | WA | Enatai Elementary | School | 2015 | 87500
|  | Enlighted | Real |  | https://www.enlightedinc.com/wp-content/uploads/2022/09/Enlighted_Casestudy_Menlo-Rev01.pdf | United States | CA | Menlo business park | Office/lab |  | 500000 |  |  |  | 2.7M |  |  | This is a 12 building project 60% lighting savings 30% HVAC savings
|  | Intesis |  |  | https://www.intesis.com/docs/librariesprovider11/case-studies/ecomt_success-story_2020.pdf | United States | WW | 3000+ Retail Stores | Retail | 2014-2017 |  |  |  |  | 20% | 3.5 |  | Integrating the Air Conditioning system into the BMS offers the possibility of generating automatic actions as soon as an event happens. For example, the AC will be instantly switched off when a fire alarm occurs. Benefits • Global reduction of energy consumption by 20%. • All stores controlled from a remote central point. • Real time alarm monitoring for effective preventive maintenance. • Interaction with other systems for e.g. the fire control, lighting, access control, and UPS. “The wide range of Intesis gateways, as well as the company’s extensive experience with the Air Conditioning manufacturers has provided to us a path to handle this project efficiently and quickly” José J.Blanco García, Retail Business Development Manager at ECOMT.
|  |  | Real |  | https://aeieng.com/news/integration-of-lighting-and-hvac-systems-new-technologies-come-of-age | United States | CA |  | Office/lab |  |  |  |  | vav
|  | Panduit | Real |  | https://www.panduit.com/content/dam/panduit/en/solutions/solution-pdf/NI-ENT-CiscoCaseStudy_CPCS64.pdf | Canada | Ontario | Cisco systems | Office | 2019 |  |  |  | vav |  |  |  | Another important goal for Cisco was to apply an expansive PoE system to deliver power to various devices in the space, including climate control and lighting. This would allow for simplified installation, flexibility, and improved reliability for powered devices. The PoE implementation would include the following PoE components to enable new IP devices: IP lighting, variable air volume (VaV) controllers, security cameras, environmental sensors, VoIP phones, and door access controls. Cisco also wanted to deploy high speed wired and wireless access.
|  | Enlighted | Real |  | https://www.enlightedinc.com/wp-content/uploads/2023/02/Enlighted_Case-Study_CSU-Long-Beach_r4.pdf | United States | CA | California State University Long Beach 110 buildings | School | 2019 | 3M sqft |  |  | zone | 15% Utility cost saving |  |  | The team partnered with Enlighted to fully commission the six-story, 101,670 square-foot Engineering and Computer Science building. This involved deploying 1,000 Enlighted LED lights with integrated sensors that enabled occupancy data to drive HVAC settings by zone. This delivered significant reductions in lighting energy use. But, they were even more pleased with the dramatic impact on HVAC energy cost, as this system accounts for a much larger portion of their energy costs. Being able to program setbacks by zone and set fans to run only when needed, rather than constantly delivered real results.
|  | Enlighted | Real |  | https://www.enlightedinc.com/wp-content/uploads/2022/09/Enlighted_Casestudy_ATT_p1r2.pdf | United States |  | 240 AT&T properties | Various | 2022 | 20M sqft |  |  |  | Estimated $8M/yr |  |  | AT&T estimates that the initial 20-million square foot retrofit project is saving the company around $8 million a year in lighting-energy expense. Once the rollout is complete across the entire portfolio, Enlighted’s system could reduce AT&T’s energy consumption by 195 gigawatt-hours, which could net the firm $200 million in savings during a span of 10 years.
IEEE |  |  | Real |  | https://www.researchgate.net/publication/321722887_Impact_of_Building_Automation_Control_Systems_on_Energy_Efficiency-University_Building_Case_Study |  |  |  | School | 2015 |  |  |  |  | Roughly 10% overall savings in a year |  |  | Modern BACS are systems with control and monitoring functions distributed in a network nodes installed in buildings. These functions operate with technical buildings infrastructure systems like a heating, ventilation, air-conditioning (HVAC), lighting, shading, access control etc
IEEE |  |  | Real |  | https://www.researchgate.net/publication/277751115_Lighting_Control_and_Monitoring_for_Energy_Efficiency_A_Case_Study_Focused_on_the_Interoperability_of_Building_Management_Systems | Other | Turin | Polytechnic University of Turin | Office | 2015 |  |  |  |  | 36% Overall Energy savings per hour with lights on 60% overall energy savings per hours with lights on in admin offices |  |  | The paper presents some results of a project carried out within the 7th European Research Framework Program, aimed at developing an event–driven user-centric middleware for monitoring and managing energy consumption in public buildings. One of the strengths of the designed system is to allow an easy integration of heterogeneous technologies and their hardware independent interoperability. This is a feature of great importance to existing buildings, where standing controls could be integrated with new technologies to enhance a greater building energy efficiency. The functionality of the system has been tested in some representative spaces of existing public buildings. Control strategies and hardware infrastructures have been defined to manage the operation of HVAC and lighting plants. The test rooms saw far more hours with lights on, but had far lower consumption/ hrs with lights on.
DOE EERE |  |  | Real |  | https://www.mncee.org/sites/default/files/report-files/EE0008191_PoE_Case_Study_SinclairHotel.pdf | United States | TX | Mariott Sinclair Hotel | Hotel | 2020 | 164000 |  |  | VRF
|  | Cisco | Real |  | https://www.cisco.com/c/en/us/solutions/collateral/enterprise-networks/dna-spaces/cisco-penn1-case-study.pdf | United States | New York, NY | Penn 1 Plaza | Office | 2022 | 42000 | [6 empty] | PENN 1, a 42,000-square-foot Midtown Manhattan building constructed in the 1970s, was never designed to be smart or data driven. But with a foundational network featuring Cisco Catalyst® 9000 switches and access points, PoE technology that provides data connectivity and electrical power for the building’s subsystems, and a single interface——Cisco Spaces——for integrating and visualizing the data from those systems, PENN 1 is showcasing new levels of innovation, flexibility, and sustainability. • Created a smart building with innovative, fully interconnected subsystems • Leveraged automation and PoE to reduce power consumption and costs by an estimated 50 percent or more • Dramatically improved workplace comfort, flexibility, and sustainability
|  | Intesis | Real |  | https://www.intesis.com/docs/librariesprovider11/case-studies/case-study-baku-white-house.pdf?sfvrsn=54458bd7_3 | Other | Baku | White home in Baku | Luxury villa | 2022 | 7500 |  |  |  | Estimated 60% |  |  | KNX Award winning project KNX connected devices can be controlled remotely and will manage a wide range of functions, including lighting, blinds and shutters, heating, ventilation and air conditioning (HVAC), security systems, energy management, audio video, white goods, and displays.
|  | Intesis and JUNG | Real |  | https://www.intesis.com/docs/librariesprovider11/case-studies/intesis_case_study_jung_korea.pdf?sfvrsn=1aad0d7_9 | Other | Sejong City | Ray Castle Hotel and Resort | Hotel | 2022 | [7 empty] | In the project various local installations such as air conditioning, lighting, and access control devices were configured with ETS software. HMS products that provide data connectivity between almost all major industrial network equipment and IIoT applications can easily and securely transmit data from various industrial equipment communicating with Ethernet/ fieldbus/serial protocols to IT systems and IoT software. The fact that there is no need to purchase additional facilities is a big advantage in terms of cost efficiency.
|  | Intesis and Cuber (Netherlands) | Real |  | https://www.intesis.com/docs/librariesprovider11/case-studies/intesis_case_study_cuber.pdf?sfvrsn=813ac6d7_13 | Other |  | Various holiday chalets | Holiday Homes | 2022 | [7 empty] | A Cuber (The app to control the system by phone) holiday starts with the opening of the chalet door - from the App. Turn on the lights, operate the blinds and the air conditioning, everything is controlled from the App. The objective is to combine the service of a designer hotel with the freedom of one’s own home. Cuber can use rules to set temperatures based on vacancy and room occupation for best guest experience and energy efficiency.
|  | Intesis Inelbo | Real |  | https://www.intesis.com/docs/librariesprovider11/case-studies/intesis_case_study_inelbo.pdf?sfvrsn=428614d7_10 | Other | Spain | Grocery store franchise in Spain | Retail | 2021 | [7 empty] | The project comprises electrical control equipment and energy efficiency services for indoor climate systems, sanitary hot water tanks, ventilation systems, etc. It is fully customizable to meet every shop’s requirements and it includes IoT devices that enable communication with any open control system. Lighting is controlled over DALI protocol, featuring zone sectoring, programmable schedules and automated use of daylight. Project is currently in progress, aiming at implementing the solution in +1,600 Points of Sale.
California Energy Commission |  |  | Model |  | https://www.energy.ca.gov/sites/default/files/2023-06/CEC-500-2023-039.pdf | United States | CA | University of California, Davis CA | School | 20 |  |  |  | Constant air volume, packaged central air conditioning gas furnace | 10,240 kw-hr (11%) saved from lighting hvac integration in a code compliant building | 3 | 3 years for lighting and hvac control system integration in a code compliant building | the California Energy Commission (CEC) funded CLTC to complete a pilot-scale IBCS (integrated building control system) demonstration, including HVAC integration, in an existing commercial building at the University of California (UC) campus in Davis, California. The project goal was to refine, install, and evaluate the precommercial IBCS under real-world conditions to demonstrate the feasibility of the lower-cost, integrated controls approach and validate its potential for improving commercial building energy efficiency and demand flexibility This row is for the model scenario for hvac and lighting integration in an already code compliant building
California Energy Commission |  |  | Model |  | https://www.energy.ca.gov/sites/default/files/2023-06/CEC-500-2023-039.pdf | United States | CA | University of California, Davis CA | School |  |  |  |  | Constant air volume, packaged central air conditioning gas furnace | 32,769 kw-hr (37%) saved from lighting and hvac integration including retrofit | 12.3 | 12.3 years for lighting and control system integration including retrofitting | the California Energy Commission (CEC) funded CLTC to complete a pilot-scale IBCS (integrated building control system) demonstration, including HVAC integration, in an existing commercial building at the University of California (UC) campus in Davis, California. The project goal was to refine, install, and evaluate the precommercial IBCS under real-world conditions to demonstrate the feasibility of the lower-cost, integrated controls approach and validate its potential for improving commercial building energy efficiency and demand flexibility This row is for the model scenario for hvac and lighting integration including retrofit
California Energy Commission |  |  | Model |  | https://www.energy.ca.gov/sites/default/files/2023-06/CEC-500-2023-039.pdf | United States | CA | University of California, Davis CA | School |  |  |  |  | Constant air volume, packaged central air conditioning gas furnace | 14,412 kw-hr (16%) saved from lighting, hvac, and shading integration including retrofit | 18.2 | 18.2 years for lighing, hvac and shading control system integration in a code compliant building | the California Energy Commission (CEC) funded CLTC to complete a pilot-scale IBCS (integrated building control system) demonstration, including HVAC integration, in an existing commercial building at the University of California (UC) campus in Davis, California. The project goal was to refine, install, and evaluate the precommercial IBCS under real-world conditions to demonstrate the feasibility of the lower-cost, integrated controls approach and validate its potential for improving commercial building energy efficiency and demand flexibility This row is for the model scenario for hvac, lighting and shading controls integration in an already code compliant building
California Energy Commission |  |  | Model |  | https://www.energy.ca.gov/sites/default/files/2023-06/CEC-500-2023-039.pdf | United States | CA | University of California, Davis CA | School |  |  |  |  | Constant air volume, packaged central air conditioning gas furnace | 36,941 kw-hr (41%) saved from lighting, hvac, and shading integration including retrofit | 17.2 | 17.2 years for lighting, hvac and shading control system including retrofit | the California Energy Commission (CEC) funded CLTC to complete a pilot-scale IBCS (integrated building control system) demonstration, including HVAC integration, in an existing commercial building at the University of California (UC) campus in Davis, California. The project goal was to refine, install, and evaluate the precommercial IBCS under real-world conditions to demonstrate the feasibility of the lower-cost, integrated controls approach and validate its potential for improving commercial building energy efficiency and demand flexibility This row is for the model scenario for hvac, lighting and shading controls integration including retrofit
To do: explore for occupancy controlled HVAC

## Lessons Learned
Project | URL | Lessons
Nexuslab Buyers Guide | https://www.nexuslabs.online/a-buyers-guide-to-hvac-lighting-controls | (not parsed yet)
Nexuslab KIPP DC | https://www.nexuslabs.online/content/case-study-kipp-dc-schools-wants-autonomy-deploys-idl-supervisory-control-fdd-and-cmms | (not parsed yet)
Cadmus 5 MN sites | https://aceee2022.conferencespot.org/event-data/pdf/catalyst_activity_32392/catalyst_activity_paper_20220810190501262_6e1bd41a_890c_4fc8_87ab_e353845d0cba | (not parsed yet)
Slipstream guidelines | https://slipstreaminc.org/publications/integrated-controls-implementation-guide | (not parsed yet)
PNNL guidelines | https://www.utilityforum.org/Data/Sites/7/media/presentations/myer-lighting-integration.pdf | (not parsed yet)
Minnesota DOT Cedar Ave Truck Station |  | The outlet controls were costly to install and would likely only be cost-effective where very large plug loads are identified
Minnesota DOT Cedar Ave Truck Station |  | Overall, lighting controls implementation was straightforward.
Minnesota DOT Cedar Ave Truck Station |  | Once lighting integration with HVAC is complete, alarms should be set to ensure that it remains functional; lighting systems will not alarm if that connection goes down
Minnesota DOT Cedar Ave Truck Station |  | Mapping control points between lighting and HVAC involves coordination between multiple parties; zoning pairs should be planned in advance.
Minnesota DOT Cedar Ave Truck Station |  | Lighting high-end trim was implemented to tune light levels to just enough for the task in each space; photometric calculations were used to plan this tuning and decrease time spent in the field.
Minnesota DOT Cedar Ave Truck Station |  | Plan on training someone on the building owner’s staff as commissioning is taking place so they have someone local who knows how to make any necessary adjustments.
Minnesota DOT Cedar Ave Truck Station | https://betterbuildingssolutioncenter.energy.gov/sites/default/files/attachments/ILC_Case_Studies_MnDOT.pdf | Controlled Plug Load and Zone Selection ted on the installation scope and commissioning process. Ensure that devices plugged into controlled outlets are good candidates for controls. High-energy consuming loads should be identified and controlled for maximum savings potential. Devices with a long startup time (like vending machines) should be plugged into an uncontrolled outlet. Select occupancy zones so that they cover all users of the controllable loads (like TV and audio-visual equipment) in conference rooms and common areas.
Minnesota DOT Cedar Ave Truck Station | https://betterbuildingssolutioncenter.energy.gov/sites/default/files/attachments/ILC_Case_Studies_MnDOT.pdf | User Engagement Provide a level of occupant education that matches the needs of the occupant. At the Cedar Avenue truck station, controllable outlet user guides were provided to building occupants during construction. Engage with occupants regularly to keep them updated on the best devices to plug into controlled outlets. Other locations, such as those with more occupant turnover, may need signage or regular communication about the technology.
Minnesota DOT Cedar Ave Truck Station | https://betterbuildingssolutioncenter.energy.gov/sites/default/files/attachments/ILC_Case_Studies_MnDOT.pdf | Installation and Commissioning Engage the information technology department at the beginning and keep them informed throughout the project. Make sure the electricians are educated on the installation scope and commissioning process.
CentraCare, Becker, Minnesota | https://integratedlightingcampaign.energy.gov/sites/default/files/2023-07/EED_2282_FLYER_CentraCare-FieldVal_FINAL2.pdf | Ensure the building system is a good candidate for controls integration. Certain building and mechanical system designs, such as the constant volume systems (e.g., single zone, variable volume, and temperature rooftop units) diminish the energy savings potential of controls integration, especially when combined with predictable building occupancy. All zones had to be fully unoccupied before setbacks occurred, which only happened when the building was closed. Scheduling would yield the same amount of savings.
CentraCare, Becker, Minnesota | https://integratedlightingcampaign.energy.gov/sites/default/files/2023-07/EED_2282_FLYER_CentraCare-FieldVal_FINAL2.pdf | Allow several weeks of data collection to verify lighting controls are properly integrated with the HVAC system. Verification of integration requires a few weeks of operational data (i.e., trend data) to be analyzed.
CentraCare, Becker, Minnesota | https://integratedlightingcampaign.energy.gov/sites/default/files/2023-07/EED_2282_FLYER_CentraCare-FieldVal_FINAL2.pdf | Significant energy savings can be achieved from automatic receptacle controls (ARCs). Plug loads that automatically turn off when the space was unoccupied resulted in 46 percent energy savings.
CentraCare, Becker, Minnesota | https://integratedlightingcampaign.energy.gov/sites/default/files/2023-07/EED_2282_FLYER_CentraCare-FieldVal_FINAL2.pdf | Identify high power loads to connect to automatic receptacle controls. Although the total savings was 46 percent, the average savings per receptacle was only 52 kWh. This results in $5 per receptacle saved because of the low actual energy saved. When possible, pair high power plug-in
CentraCare, Becker, Minnesota | https://integratedlightingcampaign.energy.gov/sites/default/files/2023-07/EED_2282_FLYER_CentraCare-FieldVal_FINAL2.pdf | Existing wiring scenarios can accidentally control non automatic receptacle controls. All of the receptacles in the room shared a common neutral wire. When the ARC turned off, it turned off other non-controlled receptacles. This was addressed by correcting the wiring to the noncontrolled receptacles downstream from the controlled one.
CentraCare, Becker, Minnesota | https://integratedlightingcampaign.energy.gov/sites/default/files/2023-07/EED_2282_FLYER_CentraCare-FieldVal_FINAL2.pdf | Properly label automatic receptacle controls. A guidance sheet indicated the controlled portion was on the top. However, when installed in some of the rooms, they were placed in the bottom position. This led building occupants to believe they were using the controlled receptacles, when in fact they weren’t.
City-Owned building, St. Paul, Minnesota | https://integratedlightingcampaign.energy.gov/sites/default/files/2023-07/EED_2407_FLYER_StPaul-FieldVal_FINAL2.pdf | Ensure product and system compatibility. Despite lighting system communicating via BACnet, integration with HVAC controls was a challenge. The lighting network and HVAC controls network were not instantly interoperable, as a result the lighting vendor had to make firmware and other modifications to allow the systems to communicate.
City-Owned building, St. Paul, Minnesota | https://integratedlightingcampaign.energy.gov/sites/default/files/2023-07/EED_2407_FLYER_StPaul-FieldVal_FINAL2.pdf | Allow extra coordination time for the first integration project. It took several months and multiple discussions among the St. Paul’s IT staff, the lighting commissioning agent, technical support team, and the local HVAC controls contractor to resolve the network communication issues.
City-Owned building, St. Paul, Minnesota | https://integratedlightingcampaign.energy.gov/sites/default/files/2023-07/EED_2407_FLYER_StPaul-FieldVal_FINAL2.pdf | Anticipate that a commissioning agent will need to make field adjustments based on real-world user needs. The commissioning agent needed to make some adjustments to the designed light levels and lighting/plug load controls based on occupant feedback.
City-Owned building, St. Paul, Minnesota | https://integratedlightingcampaign.energy.gov/sites/default/files/2023-07/EED_2407_FLYER_StPaul-FieldVal_FINAL2.pdf | Much of the equipment could be installed by electricians who don’t specialize in integrating advanced systems. The lighting and plug load system installations were straightforward and completed by the city’s staff electricians. -Building mechanical design drives integration success. Multi-zone CAV systems are not ideal for lighting integration. All the zones had to be unoccupied before a setback occurred. This resulted in no savings from occupancy-based setbacks.
City-Owned building, St. Paul, Minnesota | https://integratedlightingcampaign.energy.gov/sites/default/files/2023-07/EED_2407_FLYER_StPaul-FieldVal_FINAL2.pdf | Occupancy levels dictate energy savings and return on investment. Buildings with predictable constant occupancy may not be benefit from integration. Besides the multi-zone CAV limitation, the building staff had a regular schedule and were in the building most of the day, which meant there was no significant savings from occupancy-based setbacks.
City-Owned building, St. Paul, Minnesota | https://integratedlightingcampaign.energy.gov/sites/default/files/2023-07/EED_2407_FLYER_StPaul-FieldVal_FINAL2.pdf | Develop methods to periodically verify that systems are still integrated (e.g., 3, 6, and 12 months after initial integration). During a particularly cold week, the temperature was manually adjusted, which interrupted the integration of the mechanical and lighting systems. This was only discovered because the building was still being monitored as part of this study.
City-Owned building, St. Paul, Minnesota | https://integratedlightingcampaign.energy.gov/sites/default/files/2023-07/EED_2407_FLYER_StPaul-FieldVal_FINAL2.pdf | Train building owner/operator staff during commissioning. Once commissioning is completed by the vendor, it is beneficial to assign a local staff who can take ownership of the controls and can adjust settings as appropriate.
Hennepin County Building, Minnesota | https://integratedlightingcampaign.energy.gov/sites/default/files/2023-07/EED_2406_FLYER_Hennepin-FieldVal_FINAL2.pdf | Lighting and mechanical integration requires coordination with many more parties than a standard project with stand-alone systems. The project required close coordination between the County, the building’s property management firm, clinic staff, the lighting control vendor, and the contractor; this presented some challenges. For example, mapping control points between lighting and HVAC zones involved advanced planning and coordination between the electricians, lighting controls specialists, mechanical contractors, and building staff.
Hennepin County Building, Minnesota | https://integratedlightingcampaign.energy.gov/sites/default/files/2023-07/EED_2406_FLYER_Hennepin-FieldVal_FINAL2.pdf | Lighting software needs to be current and contain compatible firmware for successful integration. Originally expected to be plug and play, the lighting system required updates to integrate with HVAC system. The lighting vendor had to push current versions of software and firmware to devices. Plan for recurring updates and schedule them in advance.
Hennepin County Building, Minnesota | https://integratedlightingcampaign.energy.gov/sites/default/files/2023-07/EED_2406_FLYER_Hennepin-FieldVal_FINAL2.pdf | Occupants can unknowingly bypass automatic receptacle controls. Even though the plug load integration was successful, the 22 automatic receptacle controls that were installed did not yield any data. It was determined that users may have bypassed the controlled receptacles or may have been confused on which was the controlled receptacle versus the standard constant-on receptacle. The values in the savings facts are based on modeled results.
Hennepin County Building, Minnesota | https://integratedlightingcampaign.energy.gov/sites/default/files/2023-07/EED_2406_FLYER_Hennepin-FieldVal_FINAL2.pdf | Spaces lighted primarily by decorative fixtures are harder to integrate. The large exercise floor with treadmills in the fitness center had decorative fixtures that were harder to integrate into the platform. The solution was to use a tubular LED retrofit coupled to an independent control module.
Hennepin County Building, Minnesota | https://integratedlightingcampaign.energy.gov/sites/default/files/2023-07/EED_2406_FLYER_Hennepin-FieldVal_FINAL2.pdf | Occupant education is essential. Lack of energy savings data revealed that occupants may have bypassed the controlled receptacles or may have been confused on which receptacles were controlled versus constant-on. Training occupants on how the lighting controls work is key to adoption, which would yield better energy savings results. Automatic receptacle controls are a new concept for some and informational sheet explaining how it worked and which loads/devices were ideal for controlled usage were shared with the occupants however, additional guidance may have helped.
Hennepin County Building, Minnesota | https://integratedlightingcampaign.energy.gov/sites/default/files/2023-07/EED_2406_FLYER_Hennepin-FieldVal_FINAL2.pdf | Large buildings or spaces allow for more occupant response HVAC sequences. This field evaluation only involved a portion of the first (7,300 ft2) of a 15-story office tower. This hindered overall HVAC energy performance at the system level. Many potential AHU-level control improvements were omitted or constrained because the HVAC systems served many floors that did not include the new zone controls.
Hennepin County Building, Minnesota | https://integratedlightingcampaign.energy.gov/sites/default/files/2023-07/EED_2406_FLYER_Hennepin-FieldVal_FINAL2.pdf | Train building owner/operator staff during commissioning. Once the commissioning is completed by the vendor, it is beneficial to have local onsite staff who can make necessary adjustments as appropriate.
University of Minnesota | https://integratedlightingcampaign.energy.gov/sites/default/files/2023-07/EED_1581_FLYER_UM-FieldVal_FINAL2.pdf | Plan for multiple commissioning visits. Although the lighting vendor assisted through the entirety of the project which facilitated the integration, commissioning still required significant time and multiple trips.
University of Minnesota | https://integratedlightingcampaign.energy.gov/sites/default/files/2023-07/EED_1581_FLYER_UM-FieldVal_FINAL2.pdf | Integrating the lighting controls with HVAC system may be complex. The University of Minnesota had a novel port naming system. The lighting vendor faced some challenges when configuring both systems to communicate with each other.
University of Minnesota | https://integratedlightingcampaign.energy.gov/sites/default/files/2023-07/EED_1581_FLYER_UM-FieldVal_FINAL2.pdf | Establish methods to determine if integration failed or stopped. Lighting systems do not include a notification system to indicate when the connection with the HVAC system has been interrupted, therefore a mechanism for determining when the integration has stopped needs to be developed.
University of Minnesota | https://integratedlightingcampaign.energy.gov/sites/default/files/2023-07/EED_1581_FLYER_UM-FieldVal_FINAL2.pdf | Verify wiring needs of components in design stage. Some wall controls required a neutral wire to be fed to power the device, which required additional labor.
University of Minnesota | https://integratedlightingcampaign.energy.gov/sites/default/files/2023-07/EED_1581_FLYER_UM-FieldVal_FINAL2.pdf | Networked lighting solutions may need internet access. Involve the IT staff early in the project to ensure the controls system has a path to connect to the internet. Initial implementation was attempted without prior verification of this connection, which led to project delays and other challenges. -Label automatic receptacle controls. Many of the automatic receptacle controls (plug load controls) were installed in quad electrical boxes with standard receptacles. This meant three of the four receptacles were constantly on. Only one receptacle was controlled to turn off when the space was unoccupied, but it looked similar to resting mode. Color-coding or some other method of identification is recommended so users know which receptacles are controlled.
University of Minnesota | https://integratedlightingcampaign.energy.gov/sites/default/files/2023-07/EED_1581_FLYER_UM-FieldVal_FINAL2.pdf | Label automatic receptacle controls. Many of the automatic receptacle controls (plug load controls) were installed in quad electrical boxes with standard receptacles. This meant three of the four receptacles were constantly on. Only one receptacle was controlled to turn off when the space was unoccupied, but it looked similar to resting mode. Color-coding or some other method of identification is recommended so users know which receptacles are controlled.
University of Minnesota | https://integratedlightingcampaign.energy.gov/sites/default/files/2023-07/EED_1581_FLYER_UM-FieldVal_FINAL2.pdf | Lighting and HVAC zones should be planned. Mapping control points between lighting and HVAC requires coordination between multiple parties: electricians, lighting controls person, mechanical contractors, and building staff.
University of Minnesota | https://integratedlightingcampaign.energy.gov/sites/default/files/2023-07/EED_1581_FLYER_UM-FieldVal_FINAL2.pdf | Educate building occupants about advanced or novel features. Training occupants on the purpose and operation of lighting and receptac
University of Minnesota | https://integratedlightingcampaign.energy.gov/sites/default/files/2023-07/EED_1581_FLYER_UM-FieldVal_FINAL2.pdf | Train facility operators and onsite staff during commissioning. Once the commissioning agent is complete, it is beneficial to have competent local on-site staff to make necessary adjustments going forward.
Denver Water Administration Building | https://betterbuildingssolutioncenter.energy.gov/sites/default/files/attachments/ILC-Case%20Study-DenverWater.pdf | INCLUDE KEY STAKEHOLDERS IN INITIAL CONVERSATIONS. When the project started, the sustainability/energy management roles did not exist; however, their design input at the outset of the project would have been ideal. The agency is building another treatment plant now and Hutchinson is pushing for a useful metering approach up front with the project designers.
Denver Water Administration Building | https://betterbuildingssolutioncenter.energy.gov/sites/default/files/attachments/ILC-Case%20Study-DenverWater.pdf | INTEGRATE METERING IN THE PROJECT DESIGN. Metering was part of the project’s electrical system setup, with power meters added in at the end. Hutchinson believes it would have been better to fully integrate sub-metering from the start for a more streamlined outcome. Beyond submetering, the team gained some additional wisdom from reviewing the project and its outcomes:
Denver Water Administration Building | https://betterbuildingssolutioncenter.energy.gov/sites/default/files/attachments/ILC-Case%20Study-DenverWater.pdf | DEFINE SYSTEM OWNERSHIP UP FRONT. There has been discussion about who should have ownership over the systems, including whose budget its installation and upkeep should come from, and who will be the administrator. It is best to define all of this before project start.
Denver Water Administration Building | https://betterbuildingssolutioncenter.energy.gov/sites/default/files/attachments/ILC-Case%20Study-DenverWater.pdf | IMPLEMENT ENTERPRISE ENERGY CONTROLS VIEWING SOFTWARE. Looking back, the team would like to have an overarching software that would provide a comprehensive view of building energy use across systems. Currently, a separate software system must be used to look at lighting energy use and compare it side by side with HVAC energy use to determine building performance.
Theodore Roosevelt Building | https://integratedlightingcampaign.energy.gov/sites/default/files/2022-04/ILC-Case%20Study-OPM-FINAL.pdf | CHECK SYSTEM COMPATIBILITY. While trying to integrate Lutron with the Siemens HVAC system, there were challenges getting the systems to communicate because the HVAC controls are on the local area network (LAN) and the Lutron system is cloud-based. The workaround can be inconvenient but is resolvable. This requires a hardwire to the Lutron server, housing it in an office, and programming all the changes in a selected location. Future recommendations include checking system compatibility and network requirements before making the investment.
Theodore Roosevelt Building | https://integratedlightingcampaign.energy.gov/sites/default/files/2022-04/ILC-Case%20Study-OPM-FINAL.pdf | PARTNER WITH IT TEAM. Compatibility challenges are prevented by establishing a partnership with the Information Technology team at the onset of the project. To achieve a seamless integration, IT built two new servers and installed two network interface communication cards in each server to allow communication between the LAN networks.
Theodore Roosevelt Building | https://integratedlightingcampaign.energy.gov/sites/default/files/2022-04/ILC-Case%20Study-OPM-FINAL.pdf | GET TENANT BUY-IN. OPM’s facilities management team recommends keeping tenants informed of decisions, overall project progress, and how it affects them. The greater their involvement, the greater the success of the project. uFIND THE RIGHT CONTRACTOR. For government buildings, OPM’s facilities management team suggests finding a contracting officer familiar with ESPC. The team recommends using the Department of Energy’s Golden Field Office as a resource.
Kaier Permanenete | https://www.willdan.com/casestudies/Kaiser-Permanente-HVAC-Case-Study.pdf | Convert HVAC units from constant air volume (CAV) to variable air volume (VAV)
Kaier Permanenete | https://www.willdan.com/casestudies/Kaiser-Permanente-HVAC-Case-Study.pdf | Implement central plant optimization strategies
Kaier Permanenete | https://www.willdan.com/casestudies/Kaiser-Permanente-HVAC-Case-Study.pdf | Revise equipment schedules to shut off during unoccupied times
Kaier Permanenete | https://www.willdan.com/casestudies/Kaiser-Permanente-HVAC-Case-Study.pdf | Implement supply air temperature reset strategies
Kaier Permanenete | https://www.willdan.com/casestudies/Kaiser-Permanente-HVAC-Case-Study.pdf | Implement economizer repairs for air handler units
Kaier Permanenete | https://www.willdan.com/casestudies/Kaiser-Permanente-HVAC-Case-Study.pdf | Conduct upgrades of interior and exterior lighting
Intesis systems in retail stores | https://www.intesis.com/docs/librariesprovider11/case-studies/ecomt_success-story_2020.pdf | One of the most significant challenges in the project was to find a product able to handle large number of communication protocols efficiently. On one hand, the Air Conditioning sector is full of different manufacturers, each one using its own internal communication language. On the other hand, the Building Management Systems can be based on different standard protocols. Therefore, to be able to control the Air Conditioning units from the BMS, it is required to install gateways capable of interpreting the protocols on both sides. The ideal solution was to find a single gateway manufacturer able to offer a wide range of products approved by the AC manufacturers, and compatible with the most common building standard protocols. Moreover, having a single gateway manufacturer helps reducing the price of the project too.
Affiliated Engineers | https://aeieng.com/news/integration-of-lighting-and-hvac-systems-new-technologies-come-of-age | Previously, building occupants may have tried to override programmed controls and then compromised intended system performance. With operators now being able to easily reprogram locations where light levels are too low (daylighting calibration) or too high (too much light), or there is a frustrating occ sensor actuation (bad positioning), keeping the building tuned to the optimum performance at which it was intended to operate is much easier.
IEEE Turin Polytechnic University | https://www.researchgate.net/publication/277751115_Lighting_Control_and_Monitoring_for_Energy_Efficiency_A_Case_Study_Focused_on_the_Interoperability_of_Building_Management_Systems | the choice of measuring the Ewp indirectly, by measuring the environment brightness through ceiling-mounted or suspended sensors, implied a complex calibration process. Installing illuminance sensors directly on the work plane seems to be a more reliable solution for future applications
IEEE Turin Polytechnic University | https://www.researchgate.net/publication/277751115_Lighting_Control_and_Monitoring_for_Energy_Efficiency_A_Case_Study_Focused_on_the_Interoperability_of_Building_Management_Systems | for both ADMIN and DITER offices, the energy performance actually observed in real rooms is strongly influenced by occupants’ behavior (especially as for the attitude to switch lights on and to keep then on during the working hours). As a consequence, the consumption may significantly differ from what expected during the design stage (when all decisions are based on simulation results)
Sinclair Hotel, Fort Worth, TX | https://www.mncee.org/sites/default/files/report-files/EE0008191_PoE_Case_Study_SinclairHotel.pdf | Repurposing older buildings into hotels can be a cost- effective and environmentally sound option.
Sinclair Hotel, Fort Worth, TX | https://www.mncee.org/sites/default/files/report-files/EE0008191_PoE_Case_Study_SinclairHotel.pdf | Each PoE device is networked with its own IP address, allowing individual device control and monitoring to manage building energy consumption.
Sinclair Hotel, Fort Worth, TX | https://www.mncee.org/sites/default/files/report-files/EE0008191_PoE_Case_Study_SinclairHotel.pdf | A dedicated IT staff assists in the operation and maintenance of the PoE and DC system.
Sinclair Hotel, Fort Worth, TX | https://www.mncee.org/sites/default/files/report-files/EE0008191_PoE_Case_Study_SinclairHotel.pdf | Using DC electricity to power the lighting, heating, and cooling in the hotel provided ease, affordability, and sustainability